## Original
System	Type	Brand	Model	Size ()	Max day		MCS FlowT	Flow	DE	Predicted		Out	Flow - Out	Heat	Carnot	AdjH4	Status	Temps	Comments
EOH2306	Air	Vaillant	VWL 125/6 A 230V S2	12	3.3	3.6		51	-51	65.586	1	6.6	44.3	10	36	2.11	Bad		Large setback then high temperature ramps up to 65C + cycling on room temp + bad % carnot
EOH2739	Air	Vaillant	VWL 125/6 A 230V S2	12	5.2	2.3		46.2	-46.2	58	1	7.8	38.4	9	41	2.75	Bad		Large setbacks, high temperature ramps, better than the last but still some 65C peaks
EOH2024	Air	Vaillant	VWL 75/6 A 230V S2	7	4.3	1.6		41.4	-41.4	50	1	6.5	34.9	7.6	40	2.92	Bad		Cycling on room temp, curve too high, low % carnot
EOH0332	Air	Vaillant	VWL 55/6 A 230V S2	5	1.6	3.1		40.2	-40.2	48	1	6.3	33.8	4.1	37	2.67	Bad		Cycling on room temp, curve too high, low % carnot, large setback
EOH2276	Air	Vaillant	VWL 125/6 A 230V S2	12	4.8	2.5		38.8	-38.8	46	1	6.4	32.4	6.9	50	3.66	Good	47@0	Weather comp set, looks good, high setback, very good % carnot
EOH2613	Air	Vaillant	VWL 125/6 A 230V S2	12	1.9	6.3		38.1	-38.1	45	1	7.7	30.4	7.5	43	2.98	OK		This is probably one of the better examples of what happens with extreme oversizing
EOH1997	Air	Vaillant	VWL 105/6 A 230V S2	10	7	1.4	40	50.4	-10.4	65	1	5.3	45.1	7.7	45	2.71	Bad	52C@-7	Very high internal temp 30C?! Is the sensor in the airing cupboard? High 53C temp is sustained through warmer conditions
EOH1918	Air	Vaillant	VWL 75/6 A 230V S2	7	4.5	1.6	50	59.3	-9.3	79	1	6.6	52.7	s	35	1.94	Bad	60C@-3	Very high temp required on coldest days but then also applied on warmer days
EOH1663	Air	Vaillant	VWL 75/6 A 230V S2	7	4	1.8	40	48	-8	61	1	6.9	41.2	4.8	44	2.78	OK/Good	48@-6	Weather comp for space heating is mostly ok, large DHW demand, setback && schedule
EOH1285	Air	Vaillant	VWL 105/6 A 230V S2	10	2.6	3.8	40	47.4	-7.4	60	1	5.8	41.6	3.7	24	1.47	Bad		Mostly low % carnot but definetly opperunity for lower wc curve
EOH0735	Air	Vaillant	VWL 75/6 A 230V S2	7	2.9	2.4	45	51.1	-6.1	66	1	6.3	44.8	7.8	42	2.54	Bad		Cycling on room temp, curve too high, low % carnot
EOH0901	Air	Vaillant	VWL 75/6 A 230V S2	7	6.7	1.0	45	50.7	-5.7	65	1	6.6	44.1	6.2	40	2.53	Bad	50@-2	WC Set too high, erratic control
EOH1686	Air	Vaillant	VWL 105/6 A 230V S2	10	3.8	2.6	45	50.4	-5.4	65	1	6.2	44.2	9	44	2.63	Bad		WC set way to high, used very intermittently
EOH3035	Air	Vaillant	VWL 55/6 A 230V S2	5	3	1.7	45	50.2	-5.2	64	1	5.1	45.1	5.2	40	2.35	Bad		WC set too high, but partly required by intermittent use
EOH2887	Air	Vaillant	VWL 75/6 A 230V S2	7	4.77	1.5	40	44.9	-4.9	56	1	4.8	40.1	5.2	44	2.85	Good		High WC Required
EOH2430	Air	Vaillant	VWL 55/6 A 230V S2	5	3.3	1.5	45	49.4	-4.4	63	1	5.2	44.3	4.6	40	2.46	Bad	60C@-3	High WC Required, strange DHW status on all the time, very poor dhw performance? Low % carnot
EOH1411	Air	Vaillant	VWL 55/6 A 230V S2	5	4.3	1.2	45	49.3	-4.3	63	1	5.9	43.4	4.9	41	2.58	Bad		High WC Required, but also running hotter than it needs to in milder conditions
EOH1097	Air	Vaillant	VWL 105/6 A 230V S2	10	3.2	3.1	45	48.7	-3.7	62	1	6.2	42.5	8.6	36	2.28	Bad		Cycling on room temp, WC too high
EOH2232	Air	Vaillant	VWL 75/6 A 230V S2	7	4.8	1.5	45	48.5	-3.5	62	1	5.6	42.9	6.8	44	2.72	Bad		High WC Required, but also running hotter than it needs to in milder conditions
EOH3128	Air	Vaillant	VWL 75/6 A 230V S2	7	4.2	1.7	45	48.3	-3.3	61	1	5.7	42.6	7.7	43	2.72	Bad		Very high temps, intermittent, long off periods, plenty of opportunity for lower WC
EOH1109	Air	Vaillant	VWL 75/6 A 230V S2	7	3.3	2.1	45	48.3	-3.3	61	1	6.2	42.1	3.8	35	2.18	OK		High WC Required, very low % carnot
EOH2782	Air	Vaillant	VWL 55/6 A 230V S2	5	7.1	0.7	45	46.8	-1.8	59	1	7	39.8	8	41	2.69	Bad		Very high temps, intermittent, long off periods, plenty of opportunity for lower WC
EOH1925	Air	Vaillant	VWL 55/6 A 230V S2	5	3.9	1.3	45	46.7	-1.7	59	1	5.2	41.6	5.7	41	2.64	Bad		High WC Required, but also running hotter than it needs to in milder conditions
EOH2414	Air	Vaillant	VWL 55/6 A 230V S2	5	2.7	1.9	45	46.7	-1.7	59	1	7	39.7	4.7	40	2.66	Bad		WC to high most of the time,
EOH3143	Air	Vaillant	VWL 55/6 A 230V S2	5	2.9	1.7	45	46.5	-1.5	58	1	5.9	40.6	5.2	43	2.8	Bad		WC to high, ramping, defrost pattern seen on other systems
EOH1669	Air	Vaillant	VWL 75/6 A 230V S2	7	5.4	1.3	45	46.5	-1.5	58	1	6.3	40.2	6.8	38	2.49	Bad		Mixof issues here, high WC, room temp cycling, low DHW performance
EOH0227	Air	Vaillant	VWL 75/6 A 230V S2	7	5.4	1.3	45	46.4	-1.4	58	1	5.5	40.9	7	42	2.71	Bad		High temps required but high temps during mild weather, defrost issues?
EOH0543	Air	Vaillant	VWL 125/6 A 230V S2	12	6.7	1.8	45	46.2	-1.2	58	1	5.7	40.5	8.6	45	2.9	OK		Mix of issues, high temps required, but also some boost high temps at other times, highly variable internal temp
EOH0254	Air	Vaillant	VWL 55/6 A 230V S2	5	2.5	2.0	45	46.1	-1.1	58	1	5.4	40.7	4.6	43	2.76	OK		Think there is an opportunity for less intermittent and lower WC here
EOH2544	Air	Vaillant	VWL 125/6 A 230V S2	12	6.9	1.7	45	45.6	-0.600000000000001	57	1	7.2	38.4	11.2	42	2.89	Bad		Cycling on room temp, WC too high
EOH2922	Air	Vaillant	VWL 75/6 A 230V S2	7	3.9	1.8	50	50.6	-0.600000000000001	65	1	4.9	45.7	3.2	38	2.28	Good		High WC Required, well set WC, poor % carnot
EOH1557	Air	Vaillant	VWL 55/6 A 230V S2	5	4.7	1.1	45	45.6	-0.600000000000001	57	1	5.6	40	4.2	32	2.07	OK		High WC Required, defrost issues? Air circulation? Very low % carnot
EOH1328	Air	Vaillant	VWL 125/6 A 230V S2	12	4.2	2.9	50	50.2	-0.200000000000003	64	1	7.5	42.7	10.2	43	2.34	Bad		Mix of too high WC, some better WC operation, large set backs
EOH2052	Air	Vaillant	VWL 75/6 A 230V S2	7	2.6	2.7	45	45.2	-0.200000000000003	56	1	8.6	36.6	5.5	40	2.67	Good		Weather comp is mid 40s, large setback/schedule. Mostly low % carnot
EOH1327	Air	Vaillant	VWL 75/6 A 230V S2	7	2.5	2.8	50	50	0	64	1	7.5	42.5	6.8	42	2.61	OK		Very high DHW demand coupled with high DHW temps, large setback on space heating..
EOH0457	Air	Vaillant	VWL 55/6 A 230V S2	5	4.5	1.1	45	45	0	56	1	6.3	38.6	5.5	40	2.69	Bad		High temps required, at max capacity, high temps required 51C..cycling on room.. weather comp too high at other times
EOH0033	Air	Vaillant	VWL 125/6 A 230V S2	12	4.8	2.5	45	45	0	56	1	7.3	37.6	9.4	37	2.52	OK		Something strange here, might be buffer distortion related?
EOH0455	Air	Vaillant	VWL 55/6 A 230V S2	5	3.5	1.4	45	44.9	0.100000000000001	56	1	3.6	41.3	5	39	2.4	Bad		Mix of high temps required, running to hot at other times, low % carnot
EOH2765	Air	Vaillant	VWL 125/6 A 230V S2	12	3.9	3.1	45	44.8	0.200000000000003	56	1	5.9	38.9	9.6	42	2.76	Bad		WC to high.
EOH0630	Air	Vaillant	VWL 55/6 A 230V S2	5	3.8	1.3	45	44.7	0.299999999999997	55	1	4.9	39.8	5.7	45	2.92	Bad		maaxed out on coldest day for periods, 48C, high temps during milder weather..
EOH2262	Air	Vaillant	VWL 125/6 A 230V S2	12	5.9	2.0	49	48.6	0.399999999999999	62	1	7.6	41.1	12.2	42	2.75	Bad		very high temp and lots of DHW, WC too high
EOH1018	Air	Vaillant	VWL 125/6 A 230V S2	12	3.8	3.2	50	49.5	0.5	63	1	7.1	42.5	10.2	39	2.45	Bad		high hot water temps, wc too high,
EOH0432	Air	Vaillant	VWL 75/6 A 230V S2	7	4.3	1.6	45	43.8	1.2	54	1	7.8	36.1	8.1	36	2.6	Bad		Too high WC, cycling on room temp
EOH2036	Air	Vaillant	VWL 75/6 A 230V S2	7	2.9	2.4	45	43.6	1.4	54	1	4.7	38.9	5.5	38	2.48	Bad		WC to high
EOH0667	Air	Vaillant	VWL 55/6 A 230V S2	5	4.6	1.1	45	43.6	1.4	54	1	5.8	37.8	5.1	37	2.52	OK		temperature sensor in garage?? very high temps required, some set backs but not a lot off room to reduce
EOH2168	Air	Vaillant	VWL 125/6 A 230V S2	12	5.4	2.2	50	48.5	1.5	62	1	7.2	41.3	10.2	41	2.66	Bad		WC too high
EOH1993	Air	Vaillant	VWL 55/6 A 230V S2	5	3.7	1.4	45	43.3	1.7	53	1	6.5	36.8	4.3	42	2.95	Bad		WC too high, control all over the place
EOH1666	Air	Vaillant	VWL 125/6 A 230V S2	12	4.9	2.4	45	43.1	1.9	53	1	6.3	36.7	9	43	2.95	Bad		WC too high
EOH0495	Air	Vaillant	VWL 125/6 A 230V S2	12	8	1.5	45	43	2	53	1	5.7	37.3	8.3	41	2.81	Bad		WC too high, though not too bad at times, temps are often low 40s but could be lower as cyclinng on room temp
EOH2804	Air	Vaillant	VWL 75/6 A 230V S2	7	5.3	1.3	45	42.7	2.3	52	1	4.8	37.9	8.1	43	2.95	Bad		WC too high. Cycling on room temp but also low room temps
EOH0038	Air	Vaillant	VWL 55/6 A 230V S2	5	2	2.5	45	42.5	2.5	52	1	7.7	34.8	5.3	42	2.94	Bad		WC too high. Cycling on room temp but also low room temps
EOH1365	Air	Vaillant	VWL 55/6 A 230V S2	5	2.9	1.7	45	42.4	2.6	52	1	5.5	36.8	4	41	2.79	OK		Bit of mixture here of WC that looks ok and some hotter boosts
EOH0184	Air	Vaillant	VWL 55/6 A 230V S2	5	2.4	2.1	55	52.4	2.6	68	1	6.8	45.6	3.8	39	2.23	Bad/OK		WC ok but DHW not right
EOH2612	Air	Vaillant	VWL 75/6 A 230V S2	7	2.9	2.4	45	42.3	2.7	52	1	5.4	36.8	3.9	37	2.43	OK		Bit of a mix, schedule/setback leads to high temps on recovery, but then WC after is ok
EOH1249	Air	Vaillant	VWL 55/3 A 230V	5	2.7	1.9	50	47.3	2.7	60	1	6.6	40.7	3.7	33	2.04	Bad		WC too high, cycling on room temps
EOH2488	Air	Vaillant	VWL 125/6 A 230V S2	12	6	2.0	45	42.1	2.9	51	1	5.8	36.4	7.4	44	3.08	Good		High temps required
EOH0809	Air	Vaillant	VWL 75/6 A 230V S2	7	3.9	1.8	50	47.1	2.9	59	1	6.7	40.4	7.3	40	2.56	Bad		WC too high, cycling on room temps
EOH2897	Air	Vaillant	VWL 75/6 A 230V S2	7	2.3	3.0	50	47	3	59	1	6.8	40.2	6.3	42	2.55	Bad		Bit of a mix, but WC is too high for extended periods, driven by return from setback
EOH0539	Air	Vaillant	VWL 75/6 A 230V S2	7	2.2	3.2	45	41.9	3.1	51	1	5.8	36.1	5.7	44	3.01	Bad		very low space heating requirement, short high temp spikes
EOH2769	Air	Vaillant	VWL 55/6 A 230V S2	5	3.8	1.3	50	46.8	3.2	59	1	4.9	41.9	5	42	2.69	Bad		WC too high, cycling on room temps
EOH2450	Air	Vaillant	VWL 105/6 A 230V S2	10	8.3	1.2	50	46.7	3.3	59	1	5.1	41.6	10.2	46	2.89	Bad		Control issue with DHW and WC too high, cycling on room temps
EOH1239	Air	Vaillant	VWL 75/6 A 230V S2	7	5.3	1.3	45	41.7	3.3	51	1	5.1	36.6	5.7	43	2.96	OK		High temps required but at least some opportunity for more even lower temp,
EOH0335	Air	Vaillant	VWL 55/6 A 230V S2	5	4.4	1.1	45	41.6	3.4	50	1	5.2	36.4	3.9	41	2.84	OK		Bit of a mix in this one
EOH0464	Air	Vaillant	VWL 75/6 A 230V S2	7	4.3	1.6	50	46.6	3.4	58	1	6.8	39.8	8.4	40	2.65	Bad		WC too high, cycling on room temps
EOH0780	Air	Vaillant	VWL 55/6 A 230V S2	5	2.9	1.7	50	46.5	3.5	58	1	6.6	39.9	5	39	2.51	Bad		WC too high
EOH1544	Air	Vaillant	VWL 125/6 A 230V S2	12	5.5	2.2	50	46.4	3.6	58	1	6	40.4	9.4	43	2.83	OK		High temps required, but lower curve could be used with smaller setback
EOH1484	Air	Vaillant	VWL 105/6 A 230V S2	10	8.5	1.2	45	41.2	3.8	50	1	5.2	36	8.3	47	2.86	OK		No heat on hot water, ultrasonic or heat meter on space heat only?
EOH1985	Air	Vaillant	VWL 75/6 A 230V S2	7	2	3.5	50	46	4	57	1	8.9	37.1	5.8	40	2.74	Bad		WC too high, cycling on room temps. Very low space heating use, mostly dhw
EOH0953	Air	Vaillant	VWL 75/6 A 230V S2	7	3.6	1.9	50	45.9	4.1	57	1	7.3	38.6	8.2	41	2.69	Bad		WC too high, cycling on room temps. Very low space heating use, mostly dhw
EOH2448	Air	Vaillant	VWL 75/6 A 230V S2	7	5.7	1.2	50	45.9	4.1	57	1	6.1	39.8	4.7	40	2.55	OK		Fault mid december? Otherwise WC ok?
EOH1254	Air	Vaillant	VWL 75/6 A 230V S2	7	3.1	2.3	45	40.7	4.3	49	1	6.3	34.4	6.2	44	3.17	OK		Intermittent heating, lower more even WC could be better
EOH2524	Air	Vaillant	VWL 105/6 A 230V S2	10	5.6	1.8	50	45.4	4.6	57	1	5.8	39.6	9.6	42	2.82	Bad		poorly set weather comp, high temp ramps to 53-61 followed by off periods
EOH1279	Air	Vaillant	VWL 75/6 A 230V S2	7	3.2	2.2	50	45.3	4.7	56	1	8.3	37	6.2	42	2.91	Bad		WC too high, cycling on room temps
EOH2868	Air	Vaillant	VWL 125/6 A 230V S2	12	5.6	2.1	45	40.1	4.9	48	1	5.1	35	6.6	47	3.32	Good	42@-6C	WC is set, generally all good
EOH0172	Air	Vaillant	VWL 125/6 A 230V S2	12	6	2.0	50	44.9	5.1	56	1	6.7	38.1	7.9	45	2.99	OK		some 65C boosts, but WC is actice
EOH0380	Air	Vaillant	VWL 125/6 A 230V S2	12	5.5	2.2	50	44.9	5.1	56	1	6.7	38.2	9.6	42	2.82	Bad		WC too high + large setback + low % carnot
EOH0389	Air	Vaillant	VWL 55/6 A 230V S2	5	2.3	2.2	50	44.8	5.2	56	1	6.6	38.1	5.8	40	2.62	Bad		Very intermittent + 50+ temps
EOH1183	Air	Vaillant	VWL 55/3 A 230V	5	2	2.5	50	44.7	5.3	55	1	9	35.7	5.4	31	2.12	Bad/OK		Mostly hot water, a few days of space heating, all high temps, intermittent
EOH1334	Air	Vaillant	VWL 55/3 A 230V	5	1.5	3.3	50	44.6	5.4	55	1	6.5	38.2	5.6	37	2.4	Bad		WC too high, intermittent 55
EOH2405	Air	Vaillant	VWL 125/6 A 230V S2	12	4	3.0	50	44.5	5.5	55	1	6.6	37.9	8.9	45	2.94	Bad		Intermittent, high temp, cycling on room temp, oversized
EOH2255	Air	Vaillant	VWL 125/6 A 230V S2	12	4.5	2.7	50	44.5	5.5	55	1	6.9	37.6	11.1	43	2.86	Bad		Intermittent, high temp, cycling on room temp, oversized
EOH2988	Air	Vaillant	VWL 75/6 A 230V S2	7	2	3.5	50	44.5	5.5	55	1	7.1	37.4	5.6	43	2.84	Bad		Intermittent, high temp, cycling on room temp, oversized
EOH2122	Air	Vaillant	VWL 75/6 A 230V S2	7	4	1.8	50	44.5	5.5	55	1	5.9	38.6	7.6	40	2.68	Bad		WC too high, cycling on room temps
EOH0571	Air	Vaillant	VWL 75/6 A 230V S2	7	4.9	1.4	50	44.1	5.9	54	1	6.6	37.5	7.1	41	2.89	Bad		High temps required, Flow temps too high in mild conditions, cycling on room temp
EOH1363	Air	Vaillant	VWL 125/6 A 230V S2	12	5	2.4	50	43.8	6.2	54	1	6.4	37.4	7.9	46	3.15	OK		High temps required, a bit off cycling on room temp, but maybe limited by being oversized and perhaps interaction of buffer?
EOH3016	Air	Vaillant	VWL 125/6 A 230V S2	12	4.5	2.7	50	43.7	6.3	54	1	6.1	37.7	10.1	38	2.65	Bad		WC too high, cycling on room temps
EOH2409	Air	Vaillant	VWL 55/6 A 230V S2	5	2.4	2.1	50	43.7	6.3	54	1	6.1	37.6	4.6	37	2.43	Bad		WC too high, cycling on room temps
EOH0231	Air	Vaillant	VWL 55/3 A 230V	5	4	1.3	50	43.7	6.3	54	1	8	35.6	5.7	36	2.47	Bad		High temps required, Flow temps too high in mild conditions, cycling on room temp
EOH0682	Air	Vaillant	VWL 55/6 A 230V S2	5	3	1.7	50	43.4	6.6	53	1	7.9	35.6	4.8	40	2.89	Bad		WC too high, cycling on room temps
EOH1576	Air	Vaillant	VWL 55/6 A 230V S2	5	3.6	1.4	45	38.3	6.7	45	0	5.5	32.9	3.5	37	2.74	OK		WC was improved on this one part way through
EOH0745	Air	Vaillant	VWL 75/6 A 230V S2	7	4.8	1.5	50	42.8	7.2	52	1	6.2	36.6	5	41	2.85	Good		WC is set, seems mostly fine, low % carnot?
EOH2564	Air	Vaillant	VWL 75/6 A 230V S2	7	3.1	2.3	50	42.8	7.2	52	1	6.7	36	4.5	41	2.85	Good		WC is set, seems mostly fine, low % carnot?
EOH2212	Air	Vaillant	VWL 55/3 A 230V	5	1.9	2.6	50	42.8	7.2	52	1	6.5	36.4	5.6	36	2.47	Bad		WC too high, cycling on room temps
EOH0490	Air	Vaillant	VWL 125/6 A 230V S2	12	9.7	1.2	50	42.7	7.3	52	1	8.1	34.6	12.4	43	3.02	Bad		Poorly set weather comp, High temperature periods 53C followed by long off periods
EOH0391	Air	Vaillant	VWL 75/6 A 230V S2	7	2.3	3.0	50	42.6	7.4	52	0	6.3	36.2	6.1	39	2.3	Bad		Intermittent, WC too high
EOH2578	Air	Vaillant	VWL 125/6 A 230V S2	12	5.4	2.2	50	42.5	7.5	52	0	6.3	36.3	8.7	44	3.07	Bad		WC too high, cycling on room temps
EOH2137	Air	Vaillant	VWL 125/6 A 230V S2	12	2.8	4.3	50	42.4	7.6	52	0	6.3	36.2	8.3	44	2.96	Bad		Intermittent, WC too high
EOH1502	Air	Vaillant	VWL 75/6 A 230V S2	7	4.4	1.6	50	42.4	7.6	52	0	7	35.4	6.1	40	2.73	Good		High % dhw, LOW % carnot
EOH3003	Air	Vaillant	VWL 125/6 A 230V S2	12	7.7	1.6	45	37.1	7.9	43	0	5.4	31.7	9.3	43	3.3	OK		Mixed bag, good periods and also plenty of cycling on room temp
EOH2303	Air	Vaillant	VWL 75/6 A 230V S2	7	2.2	3.2	50	42	8	51	0	7.5	34.5	6.4	37	2.71	Bad		Intermittent, WC too high
EOH1872	Air	Vaillant	VWL 75/6 A 230V S2	7	4.8	1.5	50	41.8	8.2	51	0	7.3	34.5	4.6	44	3.11	Good		High temps required, WC set well
EOH0655	Air	Vaillant	VWL 75/6 A 230V S2	7	3.9	1.8	50	41.7	8.3	51	0	7.2	34.5	4.6	40	2.85	Good		High temps required, WC set well, switch from continuous to intermittent, low % carnot
EOH1602	Air	Vaillant	VWL 125/6 A 230V S2	12	4.7	2.6	50	41.7	8.3	51	0	4.7	36.9	7	40	2.62	OK		High temps required, oversized, low % carnot
EOH2339	Air	Vaillant	VWL 55/6 A 230V S2	5	2.5	2.0	45	36.6	8.4	42	0	0.3	36.3	3.5	48	3.06	Good		WC set well here, % carnot is high, low dhw performance and % space heating? Investigate more
EOH1392	Air	Vaillant	VWL 55/6 A 230V S2	5	1.6	3.1	50	41.6	8.4	50	0	6.3	35.4	4.7	44	3.08	OK		Intermittent heating causing higher temp boosts
EOH1186	Air	Vaillant	VWL 125/6 A 230V S2	12	5.2	2.3	50	41.6	8.4	50	0	6.6	35	8.3	44	3.14	Good		Weather comp is set, and not that high, somevery high temp DHW, cycles, slightly more difficult to pin down reason for lower performance on this.,% carnot is fairly average
EOH0047	Air	Vaillant	VWL 75/6 A 230V S2	7	6.4	1.1	45	36.6	8.4	42	0	5.7	30.9	4.4	42	3.01	Good	48@-3	Weather comp is set, high temperatures required. Room temp ~18? low % carnot
EOH2837	Air	Vaillant	VWL 75/6 A 230V S2	7	2.9	2.4	50	41.5	8.5	50	0	7.1	34.4	4.4	42	2.85	Bad		Cycling on room temp, curve too high, but not always, high temps required, low room temp (not in livingroom?)
EOH2325	Air	Vaillant	VWL 75/6 A 230V S2	7	2.9	2.4	45	36.4	8.6	42	0	4.7	31.7	8.4	41	3.04	Bad		Not cycling on room temp, but running for relatively brief periods at near max, not that hot but could be run for longer at lower flowT Low room T and low % carnot
EOH0240	Air	Vaillant	VWL 75/6 A 230V S2	7	4.6	1.5	45	36.3	8.7	42	0	5.2	31.1	4.6	45	3.49	Good		Weather comp is set, mid range % carnot, ok, possible air circulation issue, max output seems to be 5 kW?
EOH2079	Air	Vaillant	VWL 75/6 A 230V S2	7	4.2	1.7	55	46.1	8.9	58	1	6.8	39.3	5.5	42	2.8	Bad		Poorly set weather comp, High temperature periods 53C followed by long off periods
EOH0324	Air	Vaillant	VWL 75/6 A 230V S2	7	3.6	1.9	50	41.1	8.9	50	0	6.5	34.6	4.4	40	2.65	OK		System needs to run hot, room temp not that high, very distinct schedule/setback, low % carnot
EOH0411	Air	Vaillant	VWL 75/6 A 230V S2	7	3.5	2.0	50	40.9	9.1	49	0	6.1	34.8	6.3	37	2.66	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH0218	Air	Vaillant	VWL 105/6 A 230V S2	10	4.6	2.2	50	40.8	9.2	49	0	5.7	35.2	6.8	44	2.89	Bad		Non optimal curve, but mostly a DHW issue, sensor fallen out?
EOH0501	Air	Vaillant	VWL 75/6 A 230V S2	7	4.6	1.5	55	45.5	9.5	57	0	6.3	39.2	6.5	43	2.88	Bad		Very high curve, 50-55C temps, long off periods, large setback/schedules
EOH1166	Air	Vaillant	VWL 75/6 A 230V S2	7	2.1	3.3	50	40.4	9.6	48	0	6.5	33.9	5	36	2.6	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH1711	Air	Vaillant	VWL 75/6 A 230V S2	7	3	2.3	55	45.3	9.7	56	0	8.1	37.2	6.7	57	3.91	Good		Weather comp set, large setback, high % carnot!
EOH0031	Air	Vaillant	VWL 75/6 A 230V S2	7	5	1.4	50	40.2	9.8	48	0	7.4	32.8	8.1	38	2.9	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH2980	Air	Vaillant	VWL 75/6 A 230V S2	7	2.3	3.0	50	40	10	48	0	7.1	32.8	7.6	37	2.78	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH0876	Air	Vaillant	VWL 75/6 A 230V S2	7	2.7	2.6	50	39.9	10.1	48	0	6.5	33.4	7.2	42	2.94	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH0568	Air	Vaillant	VWL 55/6 A 230V S2	5	3.2	1.6	50	39.8	10.2	47	0	5.8	34	5.1	36	2.66	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH1048	Air	Vaillant	VWL 75/6 A 230V S2	7	5.1	1.4	55	44.7	10.3	55	0	5.5	39.2	5.2	45	2.99	Good		Weather comp set, DHW control is not right
EOH0562	Air	Vaillant	VWL 125/6 A 230V S2	12	7.4	1.6	50	39.5	10.5	47	0	7.4	32.2	7.4	45	3.43	Good	53@0C	Weather comp set well, but high temps required due to small rads
EOH0091	Air	Vaillant	VWL 125/6 A 230V S2	12	3.6	3.3	50	39.5	10.5	47	0	5.7	33.8	8.3	41	3	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH3033	Air	Vaillant	VWL 75/6 A 230V S2	7	4.7	1.5	50	39.4	10.6	47	0	4	35.4	7.6	41	2.84	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH0474	Air	Vaillant	VWL 55/6 A 230V S2	5	2.1	2.4	50	39.2	10.8	46	0	7.7	31.5	3.4	38	2.92	OK	46@-3C	Weather comp is set, large setback and schedules, very low % carnot
EOH1893	Air	Vaillant	VWL 75/6 A 230V S2	7	2.9	2.4	50	38.5	11.5	45	0	6	32.5	5.7	48	3.58	Good		Weather comp set fairly well, but still cycling a bit on room temp, very even indoor temperature, good % carnot
EOH3014	Air	Vaillant	VWL 55/6 A 230V S2	5	2.9	1.7	50	38.5	11.5	45	0	7.4	31.1	3.9	42	3.16	OK		Weather comp is set on this, but uses high temp boost to bring house back to temp on schedule
EOH0766	Air	Vaillant	VWL 75/6 A 230V S2	7	2.7	2.6	55	43.3	11.7	53	0	7.4	35.9	5.2	43	3.06	OK	53@0C	Weather comp is set correctly, high temps required, though large set-back
EOH1942	Air	Vaillant	VWL 75/6 A 230V S2	7	4.7	1.5	50	38.3	11.7	45	0	6.5	31.8	7.3	42	3.19	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, interesting example of lots of defrosts on room temp ramp, air circulation issues?
EOH1042	Air	Vaillant	VWL 75/6 A 230V S2	7	4.5	1.6	55	43.1	11.9	53	0	7	36.1	5.3	45	3.16	OK	50C@-8	Weather comp set, struggling a bit with max output, some hot water issues
EOH2149	Air	Vaillant	VWL 55/6 A 230V S2	5	2.5	2.0	55	43.1	11.9	53	0	6.3	36.8	3.9	44	3	OK		Mostly well set weather comp with large set back, a little room temp cycling
EOH1771	Air	Vaillant	VWL 125/6 A 230V S2	12	3.6	3.3	50	38	12	45	0	5.7	32.3	7.1	47	3.3	OK		Weather comp is set, and often low temp, struggling a bit with oversizing and some DHW control
EOH0687	Air	Vaillant	VWL 75/6 A 230V S2	7	3.5	2.0	50	37.8	12.2	44	0	7.5	30.3	4.8	43	3.18	Good		Weather comp is set well, fair setback, lots of DHWbut DHW performance is ok
EOH2568	Air	Vaillant	VWL 125/6 A 230V S2	12	5.5	2.2	50	37.7	12.3	44	0	5.7	31.9	7.5	48	3.26	Good		Weather comp is set, some DHW control issues, scheduling && setback, high % carnot interestingly
EOH1761	Air	Vaillant	VWL 105/6 A 230V S2	10	4.9	2.0	50	37.7	12.3	44	0	5.5	32.1	6.9	46	3.37	Great	37@-6!	All aligned quite well here, would usually expect higher perfromance, perhaps lower outside temperature is a factor here
EOH2011	Air	Vaillant	VWL 75/6 A 230V S2	7	3.3	2.1	55	42.6	12.4	52	0	6.2	36.5	5.2	43	3.05	Bad		Bit of a mixed bag of cycling on room temp and reasonable WC
EOH0144	Air	Vaillant	VWL 55/3 A 230V	5	1.9	2.6	50	37.6	12.4	44	0	6.4	31.2	5.6	34	1.91	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH1114	Air	Vaillant	VWL 125/6 A 230V S2	12	4.3	2.8	50	37.5	12.5	44	0	6.8	30.7	6.5	43	3.29	Good	43-53	Weather comp is set, high DHW temps but looks reasonable overall
EOH0065	Air	Vaillant	VWL 75/6 A 230V S2	7	2.5	2.8	50	37.5	12.5	44	0	6.7	30.8	6.8	43	3.31	OK		Mostly room temp cycling but curve is close
EOH0200	Air	Vaillant	VWL 75/6 A 230V S2	7	2.8	2.5	55	42.1	12.9	51	0	7	35.1	5	40	2.83	OK	37-52	Weather comp is set, but lots of variation due to schedules / set back, very low % carnot, possibly some room temp cycling
EOH2497	Air	Vaillant	VWL 75/6 A 230V S2	7	3.071	2.3	55	41.8	13.2	51	0	6.9	34.9	4.4	43	2.93	Good	45@-5	Weather comp is set, but oversized means only continuous running below 0
EOH0857	Air	Vaillant	VWL 75/6 A 230V S2	7	3.4	2.1	55	41.8	13.2	51	0	7.3	34.5	5.4	41	3.02	Good	MAX50@2C	Weather comp is set, could be reduced with higher setback, low % carnot
EOH1131	Air	Vaillant	VWL 75/6 A 230V S2	7	1.6	4.4	55	41.7	13.3	51	0	7.5	34.2	4.8	42	2.95	Bad/OK?		Mix of WC & room temp cycling, low space heating, high DHW, low % carnot
EOH0922	Air	Vaillant	VWL 75/6 A 230V S2	7	3.7	1.9	55	41.6	13.4	50	0	6.7	34.9	5.8	42	3.03	Bad	55@0C	High curve, but maybe also high temp requirement, low % carnot
EOH2466	Air	Vaillant	VWL 125/6 A 230V S2	12	8.1	1.5	50	36.4	13.6	42	0	5.4	31	11.5	41	3.16	Bad	45@-5	Not highest temp, but definetly room temp cycling, low % carnot
EOH2241	Air	Vaillant	VWL 75/6 A 230V S2	7			50	36	14	41	0	5.8	30.2	4.3	46	3.38	Good	42@-7C	Weather comp is set, looks reasonable
EOH3056	Air	Vaillant	VWL 55/6 A 230V S2	5	3.1	1.6	45	30.9	14.1	33	0	4.6	26.3	3.3	55	4.68	Good	28-30!	Very low wether comp, very high % carnot = 4.7
EOH0066	Air	Vaillant	VWL 75/6 A 230V S2	7	3.5	2.0	45	30.7	14.3	33	0	5.6	25.1	4.4	45	3.9	Good	28-33!	Very low wether comp, reasonble % carnot = 3.9
EOH0238	Air	Vaillant	VWL 55/6 A 230V S2	5	2.9	1.7	55	40.3	14.7	48	0	6.6	33.7	3.3	41	3	OK	~51@-5	Weather comp is set, needs ~50 at designt emp, low % carnot
EOH0668	Air	Vaillant	VWL 125/6 A 230V S2	12	5.6	2.1	55	40.2	14.8	48	0	6.4	33.8	7.7	45	3.26	Bad		Weather comp, large setback, weather comp increased in second winter, more room temp based cycling, weather comp too high
EOH0222	Air	Vaillant	VWL 75/6 A 230V S2	7	2.5	2.8	55	39.9	15.1	48	0	6.3	33.7	5.1	41	3	OK		Weather comp is set, maybe a bit too high at times, some room temp cycling, oversized and low % carnot, low space heating demand I think
EOH0732	Air	Vaillant	VWL 125/6 A 230V S2	12	4.8	2.5	55	39.6	15.4	47	0	6.5	33.2	6.3	46	3.25	Good		Weather comp is set, fairly continuous on coldest day
EOH0943	Air	Vaillant	VWL 125/6 A 230V S2	12	4.5	2.7	55	39.3	15.7	47	0	6.4	32.9	7.7	51	3.7	Good		Weather comp, large set back, high % carnot
EOH0286	Air	Vaillant	VWL 125/6 A 230V S2	12	3.9	3.1	55	39.2	15.8	46	0	6.7	32.5	7.4	45	3.38	Good		Weather comp, large set back
EOH1960	Air	Vaillant	VWL 125/6 A 230V S2	12	4.9	2.4	50	34.1	15.9	38	0	5.8	28.4	7.6	47	3.78	Good		Weather comp set, lots of cycling from over-sizing
EOH1738	Air	Vaillant	VWL 75/6 A 230V S2	7	3.3	2.1	55	39.1	15.9	46	0	6.9	32.2	4.6	42	3.13	Good		Weather comp with low set back (heat pump off over night)
EOH2361	Air	Vaillant	VWL 125/6 A 230V S2	12	6.1	2.0	55	39	16	46	0	7.5	31.5	7.6	46	3.53	Good		Weather comp with low set back (heat pump off over night)
EOH2436	Air	Vaillant	VWL 125/6 A 230V S2	12	5.5	2.2	55	38.9	16.1	46	0	6.6	32.3	7.4	46	3.47	Good		Weather comp with set back schedule evident
EOH1446	Air	Vaillant	VWL 125/6 A 230V S2	12	5	2.4	55	38.6	16.4	46	0	6.5	32.1	7.7	55	4	Good		Lots of cycling because of over-sizing but weather comp is active and seems ok, high % carnot 55
EOH2254	Air	Vaillant	VWL 75/6 A 230V S2	7	3.6	1.9	55	38.3	16.7	45	0	5.3	33.1	4.1	44	3.18	Good		On the whole good
EOH0005	Air	Vaillant	VWL 75/6 A 230V S2	7	3.7	1.9	55	38.1	16.9	45	0	6.8	31.4	4.4	45	3.41	Good		Weather comp with set back schedule evident
EOH2686	Air	Vaillant	VWL 75/6 A 230V S2	7	3.6	1.9	50	32.8	17.2	36	0	5.9	26.9	4.4	49	4.08	Good		Nice low flow temps e.g 30C when at 0, lots of cycling even when cold suggests fractionally oversized unit but probably ok, coldest day is 4.8 kW which is close to 5kW max anyway
EOH1233	Air	Vaillant	VWL 75/6 A 230V S2	7	5.1	1.4	55	37.8	17.2	44	0	6.2	31.5	5	44	3.4	Good
EOH0233	Air	Vaillant	VWL 125/6 A 230V S2	12	5.3	2.3	55	37.3	17.7	43	0	6.5	30.8	6.9	45	3.41	Good		A bit choppy, schedule evident, always cycling could be smoother but ok

Design	WA Flow	WA FMO				Average				Margin	2					Average
55	44.5	37.8	10.5	17.2		2.12				Total	94					2.87
50	41.3	34.6	8.7	15.4
45	38.3	31.6	6.7	13.4
40	35.2	28.5	4.8	11.5

44.5	55	55
41.3	50	50
38.3	45	45
35.2	40	40

## Sorted
System	Type	Brand	Model	Size ()	Max day		MCS FlowT	Flow	DE	Predicted		Out	Flow - Out	Heat	Carnot	AdjH4		Status	Temps	Comments
EOH2306	Air	Vaillant	VWL 125/6 A 230V S2	12	3.3	3.6		51	-51	65.586	1	6.6	44.3	10	36	2.11	2.8	Bad		Large setback then high temperature ramps up to 65C + cycling on room temp + bad % carnot
EOH2739	Air	Vaillant	VWL 125/6 A 230V S2	12	5.2	2.3		46.2	-46.2	58	1	7.8	38.4	9	41	2.75	3.2	Bad		Large setbacks, high temperature ramps, better than the last but still some 65C peaks
EOH2024	Air	Vaillant	VWL 75/6 A 230V S2	7	4.3	1.6		41.4	-41.4	50	1	6.5	34.9	7.6	40	2.92	3.5	Bad		Cycling on room temp, curve too high, low % carnot
EOH0332	Air	Vaillant	VWL 55/6 A 230V S2	5	1.6	3.1		40.2	-40.2	48	1	6.3	33.8	4.1	37	2.67	3.5	Bad		Cycling on room temp, curve too high, low % carnot, large setback
EOH1997	Air	Vaillant	VWL 105/6 A 230V S2	10	7	1.4	40	50.4	-10.4	65	1	5.3	45.1	7.7	45	2.71	2.9	Bad	52C@-7	Very high internal temp 30C?! Is the sensor in the airing cupboard? High 53C temp is sustained through warmer conditions
EOH1918	Air	Vaillant	VWL 75/6 A 230V S2	7	4.5	1.6	50	59.3	-9.3	79	1	6.6	52.7	s	35	1.94	2.7	Bad	60C@-3	Very high temp required on coldest days but then also applied on warmer days
EOH1285	Air	Vaillant	VWL 105/6 A 230V S2	10	2.6	3.8	40	47.4	-7.4	60	1	5.8	41.6	3.7	24	1.47	2.9	Bad		Mostly low % carnot but definetly opperunity for lower wc curve
EOH0735	Air	Vaillant	VWL 75/6 A 230V S2	7	2.9	2.4	45	51.1	-6.1	66	1	6.3	44.8	7.8	42	2.54	2.9	Bad		Cycling on room temp, curve too high, low % carnot
EOH0901	Air	Vaillant	VWL 75/6 A 230V S2	7	6.7	1.0	45	50.7	-5.7	65	1	6.6	44.1	6.2	40	2.53	3.0	Bad	50@-2	WC Set too high, erratic control
EOH1686	Air	Vaillant	VWL 105/6 A 230V S2	10	3.8	2.6	45	50.4	-5.4	65	1	6.2	44.2	9	44	2.63	2.9	Bad		WC set way to high, used very intermittently
EOH3035	Air	Vaillant	VWL 55/6 A 230V S2	5	3	1.7	45	50.2	-5.2	64	1	5.1	45.1	5.2	40	2.35	2.8	Bad		WC set too high, but partly required by intermittent use
EOH2430	Air	Vaillant	VWL 55/6 A 230V S2	5	3.3	1.5	45	49.4	-4.4	63	1	5.2	44.3	4.6	40	2.46	3.0	Bad	60C@-3	High WC Required, strange DHW status on all the time, very poor dhw performance? Low % carnot
EOH1411	Air	Vaillant	VWL 55/6 A 230V S2	5	4.3	1.2	45	49.3	-4.3	63	1	5.9	43.4	4.9	41	2.58	3.0	Bad		High WC Required, but also running hotter than it needs to in milder conditions
EOH1097	Air	Vaillant	VWL 105/6 A 230V S2	10	3.2	3.1	45	48.7	-3.7	62	1	6.2	42.5	8.6	36	2.28	3.0	Bad		Cycling on room temp, WC too high
EOH2232	Air	Vaillant	VWL 75/6 A 230V S2	7	4.8	1.5	45	48.5	-3.5	62	1	5.6	42.9	6.8	44	2.72	3.0	Bad		High WC Required, but also running hotter than it needs to in milder conditions
EOH3128	Air	Vaillant	VWL 75/6 A 230V S2	7	4.2	1.7	45	48.3	-3.3	61	1	5.7	42.6	7.7	43	2.72	3.0	Bad		Very high temps, intermittent, long off periods, plenty of opportunity for lower WC
EOH2782	Air	Vaillant	VWL 55/6 A 230V S2	5	7.1	0.7	45	46.8	-1.8	59	1	7	39.8	8	41	2.69	3.1	Bad		Very high temps, intermittent, long off periods, plenty of opportunity for lower WC
EOH1925	Air	Vaillant	VWL 55/6 A 230V S2	5	3.9	1.3	45	46.7	-1.7	59	1	5.2	41.6	5.7	41	2.64	3.1	Bad		High WC Required, but also running hotter than it needs to in milder conditions
EOH2414	Air	Vaillant	VWL 55/6 A 230V S2	5	2.7	1.9	45	46.7	-1.7	59	1	7	39.7	4.7	40	2.66	3.2	Bad		WC to high most of the time,
EOH3143	Air	Vaillant	VWL 55/6 A 230V S2	5	2.9	1.7	45	46.5	-1.5	58	1	5.9	40.6	5.2	43	2.8	3.1	Bad		WC to high, ramping, defrost pattern seen on other systems
EOH1669	Air	Vaillant	VWL 75/6 A 230V S2	7	5.4	1.3	45	46.5	-1.5	58	1	6.3	40.2	6.8	38	2.49	3.1	Bad		Mixof issues here, high WC, room temp cycling, low DHW performance
EOH0227	Air	Vaillant	VWL 75/6 A 230V S2	7	5.4	1.3	45	46.4	-1.4	58	1	5.5	40.9	7	42	2.71	3.1	Bad		High temps required but high temps during mild weather, defrost issues?
EOH2544	Air	Vaillant	VWL 125/6 A 230V S2	12	6.9	1.7	45	45.6	-0.600000000000001	57	1	7.2	38.4	11.2	42	2.89	3.3	Bad		Cycling on room temp, WC too high
EOH1328	Air	Vaillant	VWL 125/6 A 230V S2	12	4.2	2.9	50	50.2	-0.200000000000003	64	1	7.5	42.7	10.2	43	2.34	2.6	Bad		Mix of too high WC, some better WC operation, large set backs
EOH0457	Air	Vaillant	VWL 55/6 A 230V S2	5	4.5	1.1	45	45	0	56	1	6.3	38.6	5.5	40	2.69	3.2	Bad		High temps required, at max capacity, high temps required 51C..cycling on room.. weather comp too high at other times
EOH0455	Air	Vaillant	VWL 55/6 A 230V S2	5	3.5	1.4	45	44.9	0.100000000000001	56	1	3.6	41.3	5	39	2.4	3.0	Bad		Mix of high temps required, running to hot at other times, low % carnot
EOH2765	Air	Vaillant	VWL 125/6 A 230V S2	12	3.9	3.1	45	44.8	0.200000000000003	56	1	5.9	38.9	9.6	42	2.76	3.2	Bad		WC to high.
EOH0630	Air	Vaillant	VWL 55/6 A 230V S2	5	3.8	1.3	45	44.7	0.299999999999997	55	1	4.9	39.8	5.7	45	2.92	3.1	Bad		maaxed out on coldest day for periods, 48C, high temps during milder weather..
EOH2262	Air	Vaillant	VWL 125/6 A 230V S2	12	5.9	2.0	49	48.6	0.399999999999999	62	1	7.6	41.1	12.2	42	2.75	3.1	Bad		very high temp and lots of DHW, WC too high
EOH1018	Air	Vaillant	VWL 125/6 A 230V S2	12	3.8	3.2	50	49.5	0.5	63	1	7.1	42.5	10.2	39	2.45	3.0	Bad		high hot water temps, wc too high,
EOH1249	Air	Vaillant	VWL 55/3 A 230V	5	2.7	1.9	50	47.3	2.7	60	1	6.6	40.7	3.7	33	2.04	3.0	Bad		WC too high, cycling on room temps
EOH0809	Air	Vaillant	VWL 75/6 A 230V S2	7	3.9	1.8	50	47.1	2.9	59	1	6.7	40.4	7.3	40	2.56	3.1	Bad		WC too high, cycling on room temps
EOH2897	Air	Vaillant	VWL 75/6 A 230V S2	7	2.3	3.0	50	47	3	59	1	6.8	40.2	6.3	42	2.55	2.9	Bad		Bit of a mix, but WC is too high for extended periods, driven by return from setback
EOH0539	Air	Vaillant	VWL 75/6 A 230V S2	7	2.2	3.2	45	41.9	3.1	51	1	5.8	36.1	5.7	44	3.01	3.3	Bad		very low space heating requirement, short high temp spikes
EOH2769	Air	Vaillant	VWL 55/6 A 230V S2	5	3.8	1.3	50	46.8	3.2	59	1	4.9	41.9	5	42	2.69	3.1	Bad		WC too high, cycling on room temps
EOH2450	Air	Vaillant	VWL 105/6 A 230V S2	10	8.3	1.2	50	46.7	3.3	59	1	5.1	41.6	10.2	46	2.89	3.0	Bad		Control issue with DHW and WC too high, cycling on room temps
EOH0464	Air	Vaillant	VWL 75/6 A 230V S2	7	4.3	1.6	50	46.6	3.4	58	1	6.8	39.8	8.4	40	2.65	3.2	Bad		WC too high, cycling on room temps
EOH0780	Air	Vaillant	VWL 55/6 A 230V S2	5	2.9	1.7	50	46.5	3.5	58	1	6.6	39.9	5	39	2.51	3.1	Bad		WC too high
EOH1985	Air	Vaillant	VWL 75/6 A 230V S2	7	2	3.5	50	46	4	57	1	8.9	37.1	5.8	40	2.74	3.3	Bad		WC too high, cycling on room temps. Very low space heating use, mostly dhw
EOH0953	Air	Vaillant	VWL 75/6 A 230V S2	7	3.6	1.9	50	45.9	4.1	57	1	7.3	38.6	8.2	41	2.69	3.1	Bad		WC too high, cycling on room temps. Very low space heating use, mostly dhw
EOH2524	Air	Vaillant	VWL 105/6 A 230V S2	10	5.6	1.8	50	45.4	4.6	57	1	5.8	39.6	9.6	42	2.82	3.2	Bad		poorly set weather comp, high temp ramps to 53-61 followed by off periods
EOH1279	Air	Vaillant	VWL 75/6 A 230V S2	7	3.2	2.2	50	45.3	4.7	56	1	8.3	37	6.2	42	2.91	3.3	Bad		WC too high, cycling on room temps
EOH0380	Air	Vaillant	VWL 125/6 A 230V S2	12	5.5	2.2	50	44.9	5.1	56	1	6.7	38.2	9.6	42	2.82	3.2	Bad		WC too high + large setback + low % carnot
EOH0389	Air	Vaillant	VWL 55/6 A 230V S2	5	2.3	2.2	50	44.8	5.2	56	1	6.6	38.1	5.8	40	2.62	3.1	Bad		Very intermittent + 50+ temps
EOH1334	Air	Vaillant	VWL 55/3 A 230V	5	1.5	3.3	50	44.6	5.4	55	1	6.5	38.2	5.6	37	2.4	3.1	Bad		WC too high, intermittent 55
EOH2405	Air	Vaillant	VWL 125/6 A 230V S2	12	4	3.0	50	44.5	5.5	55	1	6.6	37.9	8.9	45	2.94	3.1	Bad		Intermittent, high temp, cycling on room temp, oversized
EOH2255	Air	Vaillant	VWL 125/6 A 230V S2	12	4.5	2.7	50	44.5	5.5	55	1	6.9	37.6	11.1	43	2.86	3.2	Bad		Intermittent, high temp, cycling on room temp, oversized
EOH2988	Air	Vaillant	VWL 75/6 A 230V S2	7	2	3.5	50	44.5	5.5	55	1	7.1	37.4	5.6	43	2.84	3.2	Bad		Intermittent, high temp, cycling on room temp, oversized
EOH2122	Air	Vaillant	VWL 75/6 A 230V S2	7	4	1.8	50	44.5	5.5	55	1	5.9	38.6	7.6	40	2.68	3.2	Bad		WC too high, cycling on room temps
EOH0571	Air	Vaillant	VWL 75/6 A 230V S2	7	4.9	1.4	50	44.1	5.9	54	1	6.6	37.5	7.1	41	2.89	3.4	Bad		High temps required, Flow temps too high in mild conditions, cycling on room temp
EOH3016	Air	Vaillant	VWL 125/6 A 230V S2	12	4.5	2.7	50	43.7	6.3	54	1	6.1	37.7	10.1	38	2.65	3.3	Bad		WC too high, cycling on room temps
EOH2409	Air	Vaillant	VWL 55/6 A 230V S2	5	2.4	2.1	50	43.7	6.3	54	1	6.1	37.6	4.6	37	2.43	3.2	Bad		WC too high, cycling on room temps
EOH0231	Air	Vaillant	VWL 55/3 A 230V	5	4	1.3	50	43.7	6.3	54	1	8	35.6	5.7	36	2.47	3.3	Bad		High temps required, Flow temps too high in mild conditions, cycling on room temp
EOH0682	Air	Vaillant	VWL 55/6 A 230V S2	5	3	1.7	50	43.4	6.6	53	1	7.9	35.6	4.8	40	2.89	3.5	Bad		WC too high, cycling on room temps
EOH2212	Air	Vaillant	VWL 55/3 A 230V	5	1.9	2.6	50	42.8	7.2	52	1	6.5	36.4	5.6	36	2.47	3.3	Bad		WC too high, cycling on room temps
EOH0490	Air	Vaillant	VWL 125/6 A 230V S2	12	9.7	1.2	50	42.7	7.3	52	1	8.1	34.6	12.4	43	3.02	3.4	Bad		Poorly set weather comp, High temperature periods 53C followed by long off periods
EOH0391	Air	Vaillant	VWL 75/6 A 230V S2	7	2.3	3.0	50	42.6	7.4	52	0	6.3	36.2	6.1	39	2.3	2.8	Bad		Intermittent, WC too high
EOH2578	Air	Vaillant	VWL 125/6 A 230V S2	12	5.4	2.2	50	42.5	7.5	52	0	6.3	36.3	8.7	44	3.07	3.3	Bad		WC too high, cycling on room temps
EOH2137	Air	Vaillant	VWL 125/6 A 230V S2	12	2.8	4.3	50	42.4	7.6	52	0	6.3	36.2	8.3	44	2.96	3.2	Bad		Intermittent, WC too high
EOH2303	Air	Vaillant	VWL 75/6 A 230V S2	7	2.2	3.2	50	42	8	51	0	7.5	34.5	6.4	37	2.71	3.5	Bad		Intermittent, WC too high
EOH2837	Air	Vaillant	VWL 75/6 A 230V S2	7	2.9	2.4	50	41.5	8.5	50	0	7.1	34.4	4.4	42	2.85	3.3	Bad		Cycling on room temp, curve too high, but not always, high temps required, low room temp (not in livingroom?)
EOH2325	Air	Vaillant	VWL 75/6 A 230V S2	7	2.9	2.4	45	36.4	8.6	42	0	4.7	31.7	8.4	41	3.04	3.6	Bad		Not cycling on room temp, but running for relatively brief periods at near max, not that hot but could be run for longer at lower flowT Low room T and low % carnot
EOH2079	Air	Vaillant	VWL 75/6 A 230V S2	7	4.2	1.7	55	46.1	8.9	58	1	6.8	39.3	5.5	42	2.8	3.2	Bad		Poorly set weather comp, High temperature periods 53C followed by long off periods
EOH0411	Air	Vaillant	VWL 75/6 A 230V S2	7	3.5	2.0	50	40.9	9.1	49	0	6.1	34.8	6.3	37	2.66	3.5	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH0218	Air	Vaillant	VWL 105/6 A 230V S2	10	4.6	2.2	50	40.8	9.2	49	0	5.7	35.2	6.8	44	2.89	3.2	Bad		Non optimal curve, but mostly a DHW issue, sensor fallen out?
EOH0501	Air	Vaillant	VWL 75/6 A 230V S2	7	4.6	1.5	55	45.5	9.5	57	0	6.3	39.2	6.5	43	2.88	3.2	Bad		Very high curve, 50-55C temps, long off periods, large setback/schedules
EOH1166	Air	Vaillant	VWL 75/6 A 230V S2	7	2.1	3.3	50	40.4	9.6	48	0	6.5	33.9	5	36	2.6	3.5	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH0031	Air	Vaillant	VWL 75/6 A 230V S2	7	5	1.4	50	40.2	9.8	48	0	7.4	32.8	8.1	38	2.9	3.7	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH2980	Air	Vaillant	VWL 75/6 A 230V S2	7	2.3	3.0	50	40	10	48	0	7.1	32.8	7.6	37	2.78	3.6	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH0876	Air	Vaillant	VWL 75/6 A 230V S2	7	2.7	2.6	50	39.9	10.1	48	0	6.5	33.4	7.2	42	2.94	3.4	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH0568	Air	Vaillant	VWL 55/6 A 230V S2	5	3.2	1.6	50	39.8	10.2	47	0	5.8	34	5.1	36	2.66	3.5	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH0091	Air	Vaillant	VWL 125/6 A 230V S2	12	3.6	3.3	50	39.5	10.5	47	0	5.7	33.8	8.3	41	3	3.5	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH3033	Air	Vaillant	VWL 75/6 A 230V S2	7	4.7	1.5	50	39.4	10.6	47	0	4	35.4	7.6	41	2.84	3.3	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH1942	Air	Vaillant	VWL 75/6 A 230V S2	7	4.7	1.5	50	38.3	11.7	45	0	6.5	31.8	7.3	42	3.19	3.6	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, interesting example of lots of defrosts on room temp ramp, air circulation issues?
EOH2011	Air	Vaillant	VWL 75/6 A 230V S2	7	3.3	2.1	55	42.6	12.4	52	0	6.2	36.5	5.2	43	3.05	3.4	Bad		Bit of a mixed bag of cycling on room temp and reasonable WC
EOH0144	Air	Vaillant	VWL 55/3 A 230V	5	1.9	2.6	50	37.6	12.4	44	0	6.4	31.2	5.6	34	1.91	2.7	Bad		Cycling on room temp, weather comp set to high, temp ramp, followed by off periods, low % carnot
EOH0922	Air	Vaillant	VWL 75/6 A 230V S2	7	3.7	1.9	55	41.6	13.4	50	0	6.7	34.9	5.8	42	3.03	3.5	Bad	55@0C	High curve, but maybe also high temp requirement, low % carnot
EOH2466	Air	Vaillant	VWL 125/6 A 230V S2	12	8.1	1.5	50	36.4	13.6	42	0	5.4	31	11.5	41	3.16	3.7	Bad	45@-5	Not highest temp, but definetly room temp cycling, low % carnot
EOH0668	Air	Vaillant	VWL 125/6 A 230V S2	12	5.6	2.1	55	40.2	14.8	48	0	6.4	33.8	7.7	45	3.26	3.5	Bad		Weather comp, large setback, weather comp increased in second winter, more room temp based cycling, weather comp too high
EOH0432	Air	Vaillant	VWL 75/6 A 230V S2	7	4.3	1.6	45	43.8	1.2	54	1	7.8	36.1	8.1	36	2.6	3.5	Bad		Too high WC, cycling on room temp
EOH2036	Air	Vaillant	VWL 75/6 A 230V S2	7	2.9	2.4	45	43.6	1.4	54	1	4.7	38.9	5.5	38	2.48	3.1	Bad		WC to high
EOH2168	Air	Vaillant	VWL 125/6 A 230V S2	12	5.4	2.2	50	48.5	1.5	62	1	7.2	41.3	10.2	41	2.66	3.1	Bad		WC too high
EOH1993	Air	Vaillant	VWL 55/6 A 230V S2	5	3.7	1.4	45	43.3	1.7	53	1	6.5	36.8	4.3	42	2.95	3.4	Bad		WC too high, control all over the place
EOH1666	Air	Vaillant	VWL 125/6 A 230V S2	12	4.9	2.4	45	43.1	1.9	53	1	6.3	36.7	9	43	2.95	3.3	Bad		WC too high
EOH0495	Air	Vaillant	VWL 125/6 A 230V S2	12	8	1.5	45	43	2	53	1	5.7	37.3	8.3	41	2.81	3.3	Bad		WC too high, though not too bad at times, temps are often low 40s but could be lower as cyclinng on room temp
EOH2804	Air	Vaillant	VWL 75/6 A 230V S2	7	5.3	1.3	45	42.7	2.3	52	1	4.8	37.9	8.1	43	2.95	3.3	Bad		WC too high. Cycling on room temp but also low room temps
EOH0038	Air	Vaillant	VWL 55/6 A 230V S2	5	2	2.5	45	42.5	2.5	52	1	7.7	34.8	5.3	42	2.94	3.4	Bad		WC too high. Cycling on room temp but also low room temps
EOH0184	Air	Vaillant	VWL 55/6 A 230V S2	5	2.4	2.1	55	52.4	2.6	68	1	6.8	45.6	3.8	39	2.23	2.7	Bad/OK		WC ok but DHW not right
EOH1183	Air	Vaillant	VWL 55/3 A 230V	5	2	2.5	50	44.7	5.3	55	1	9	35.7	5.4	31	2.12	3.3	Bad/OK		Mostly hot water, a few days of space heating, all high temps, intermittent
EOH1131	Air	Vaillant	VWL 75/6 A 230V S2	7	1.6	4.4	55	41.7	13.3	51	0	7.5	34.2	4.8	42	2.95	3.4	Bad/OK?		Mix of WC & room temp cycling, low space heating, high DHW, low % carnot
EOH2276	Air	Vaillant	VWL 125/6 A 230V S2	12	4.8	2.5		38.8	-38.8	46	1	6.4	32.4	6.9	50	3.66	3.5	Good	47@0	Weather comp set, looks good, high setback, very good % carnot
EOH2887	Air	Vaillant	VWL 75/6 A 230V S2	7	4.77	1.5	40	44.9	-4.9	56	1	4.8	40.1	5.2	44	2.85	3.1	Good		High WC Required
EOH2922	Air	Vaillant	VWL 75/6 A 230V S2	7	3.9	1.8	50	50.6	-0.600000000000001	65	1	4.9	45.7	3.2	38	2.28	2.9	Good		High WC Required, well set WC, poor % carnot
EOH2052	Air	Vaillant	VWL 75/6 A 230V S2	7	2.6	2.7	45	45.2	-0.200000000000003	56	1	8.6	36.6	5.5	40	2.67	3.2	Good		Weather comp is mid 40s, large setback/schedule. Mostly low % carnot
EOH2488	Air	Vaillant	VWL 125/6 A 230V S2	12	6	2.0	45	42.1	2.9	51	1	5.8	36.4	7.4	44	3.08	3.4	Good		High temps required
EOH2868	Air	Vaillant	VWL 125/6 A 230V S2	12	5.6	2.1	45	40.1	4.9	48	1	5.1	35	6.6	47	3.32	3.4	Good	42@-6C	WC is set, generally all good
EOH0745	Air	Vaillant	VWL 75/6 A 230V S2	7	4.8	1.5	50	42.8	7.2	52	1	6.2	36.6	5	41	2.85	3.3	Good		WC is set, seems mostly fine, low % carnot?
EOH2564	Air	Vaillant	VWL 75/6 A 230V S2	7	3.1	2.3	50	42.8	7.2	52	1	6.7	36	4.5	41	2.85	3.3	Good		WC is set, seems mostly fine, low % carnot?
EOH1502	Air	Vaillant	VWL 75/6 A 230V S2	7	4.4	1.6	50	42.4	7.6	52	0	7	35.4	6.1	40	2.73	3.3	Good		High % dhw, LOW % carnot
EOH1872	Air	Vaillant	VWL 75/6 A 230V S2	7	4.8	1.5	50	41.8	8.2	51	0	7.3	34.5	4.6	44	3.11	3.4	Good		High temps required, WC set well
EOH0655	Air	Vaillant	VWL 75/6 A 230V S2	7	3.9	1.8	50	41.7	8.3	51	0	7.2	34.5	4.6	40	2.85	3.4	Good		High temps required, WC set well, switch from continuous to intermittent, low % carnot
EOH2339	Air	Vaillant	VWL 55/6 A 230V S2	5	2.5	2.0	45	36.6	8.4	42	0	0.3	36.3	3.5	48	3.06	3.1	Good		WC set well here, % carnot is high, low dhw performance and % space heating? Investigate more
EOH1186	Air	Vaillant	VWL 125/6 A 230V S2	12	5.2	2.3	50	41.6	8.4	50	0	6.6	35	8.3	44	3.14	3.4	Good		Weather comp is set, and not that high, somevery high temp DHW, cycles, slightly more difficult to pin down reason for lower performance on this.,% carnot is fairly average
EOH0047	Air	Vaillant	VWL 75/6 A 230V S2	7	6.4	1.1	45	36.6	8.4	42	0	5.7	30.9	4.4	42	3.01	3.4	Good	48@-3	Weather comp is set, high temperatures required. Room temp ~18? low % carnot
EOH0240	Air	Vaillant	VWL 75/6 A 230V S2	7	4.6	1.5	45	36.3	8.7	42	0	5.2	31.1	4.6	45	3.49	3.7	Good		Weather comp is set, mid range % carnot, ok, possible air circulation issue, max output seems to be 5 kW?
EOH1711	Air	Vaillant	VWL 75/6 A 230V S2	7	3	2.3	55	45.3	9.7	56	0	8.1	37.2	6.7	57	3.91	3.3	Good		Weather comp set, large setback, high % carnot!
EOH1048	Air	Vaillant	VWL 75/6 A 230V S2	7	5.1	1.4	55	44.7	10.3	55	0	5.5	39.2	5.2	45	2.99	3.2	Good		Weather comp set, DHW control is not right
EOH0562	Air	Vaillant	VWL 125/6 A 230V S2	12	7.4	1.6	50	39.5	10.5	47	0	7.4	32.2	7.4	45	3.43	3.7	Good	53@0C	Weather comp set well, but high temps required due to small rads
EOH1893	Air	Vaillant	VWL 75/6 A 230V S2	7	2.9	2.4	50	38.5	11.5	45	0	6	32.5	5.7	48	3.58	3.6	Good		Weather comp set fairly well, but still cycling a bit on room temp, very even indoor temperature, good % carnot
EOH0687	Air	Vaillant	VWL 75/6 A 230V S2	7	3.5	2.0	50	37.8	12.2	44	0	7.5	30.3	4.8	43	3.18	3.5	Good		Weather comp is set well, fair setback, lots of DHWbut DHW performance is ok
EOH2568	Air	Vaillant	VWL 125/6 A 230V S2	12	5.5	2.2	50	37.7	12.3	44	0	5.7	31.9	7.5	48	3.26	3.3	Good		Weather comp is set, some DHW control issues, scheduling && setback, high % carnot interestingly
EOH1114	Air	Vaillant	VWL 125/6 A 230V S2	12	4.3	2.8	50	37.5	12.5	44	0	6.8	30.7	6.5	43	3.29	3.7	Good	43-53	Weather comp is set, high DHW temps but looks reasonable overall
EOH2497	Air	Vaillant	VWL 75/6 A 230V S2	7	3.071	2.3	55	41.8	13.2	51	0	6.9	34.9	4.4	43	2.93	3.3	Good	45@-5	Weather comp is set, but oversized means only continuous running below 0
EOH0857	Air	Vaillant	VWL 75/6 A 230V S2	7	3.4	2.1	55	41.8	13.2	51	0	7.3	34.5	5.4	41	3.02	3.5	Good	MAX50@2C	Weather comp is set, could be reduced with higher setback, low % carnot
EOH2241	Air	Vaillant	VWL 75/6 A 230V S2	7			50	36	14	41	0	5.8	30.2	4.3	46	3.38	3.5	Good	42@-7C	Weather comp is set, looks reasonable
EOH3056	Air	Vaillant	VWL 55/6 A 230V S2	5	3.1	1.6	45	30.9	14.1	33	0	4.6	26.3	3.3	55	4.68	4.1	Good	28-30!	Very low wether comp, very high % carnot = 4.7
EOH0066	Air	Vaillant	VWL 75/6 A 230V S2	7	3.5	2.0	45	30.7	14.3	33	0	5.6	25.1	4.4	45	3.9	4.2	Good	28-33!	Very low wether comp, reasonble % carnot = 3.9
EOH0732	Air	Vaillant	VWL 125/6 A 230V S2	12	4.8	2.5	55	39.6	15.4	47	0	6.5	33.2	6.3	46	3.25	3.4	Good		Weather comp is set, fairly continuous on coldest day
EOH0943	Air	Vaillant	VWL 125/6 A 230V S2	12	4.5	2.7	55	39.3	15.7	47	0	6.4	32.9	7.7	51	3.7	3.5	Good		Weather comp, large set back, high % carnot
EOH0286	Air	Vaillant	VWL 125/6 A 230V S2	12	3.9	3.1	55	39.2	15.8	46	0	6.7	32.5	7.4	45	3.38	3.6	Good		Weather comp, large set back
EOH1960	Air	Vaillant	VWL 125/6 A 230V S2	12	4.9	2.4	50	34.1	15.9	38	0	5.8	28.4	7.6	47	3.78	3.9	Good		Weather comp set, lots of cycling from over-sizing
EOH1738	Air	Vaillant	VWL 75/6 A 230V S2	7	3.3	2.1	55	39.1	15.9	46	0	6.9	32.2	4.6	42	3.13	3.6	Good		Weather comp with low set back (heat pump off over night)
EOH2361	Air	Vaillant	VWL 125/6 A 230V S2	12	6.1	2.0	55	39	16	46	0	7.5	31.5	7.6	46	3.53	3.7	Good		Weather comp with low set back (heat pump off over night)
EOH2436	Air	Vaillant	VWL 125/6 A 230V S2	12	5.5	2.2	55	38.9	16.1	46	0	6.6	32.3	7.4	46	3.47	3.6	Good		Weather comp with set back schedule evident
EOH1446	Air	Vaillant	VWL 125/6 A 230V S2	12	5	2.4	55	38.6	16.4	46	0	6.5	32.1	7.7	55	4	3.5	Good		Lots of cycling because of over-sizing but weather comp is active and seems ok, high % carnot 55
EOH2254	Air	Vaillant	VWL 75/6 A 230V S2	7	3.6	1.9	55	38.3	16.7	45	0	5.3	33.1	4.1	44	3.18	3.5	Good		On the whole good
EOH0005	Air	Vaillant	VWL 75/6 A 230V S2	7	3.7	1.9	55	38.1	16.9	45	0	6.8	31.4	4.4	45	3.41	3.6	Good		Weather comp with set back schedule evident
EOH2686	Air	Vaillant	VWL 75/6 A 230V S2	7	3.6	1.9	50	32.8	17.2	36	0	5.9	26.9	4.4	49	4.08	4.0	Good		Nice low flow temps e.g 30C when at 0, lots of cycling even when cold suggests fractionally oversized unit but probably ok, coldest day is 4.8 kW which is close to 5kW max anyway
EOH1233	Air	Vaillant	VWL 75/6 A 230V S2	7	5.1	1.4	55	37.8	17.2	44	0	6.2	31.5	5	44	3.4	3.7	Good
EOH0233	Air	Vaillant	VWL 125/6 A 230V S2	12	5.3	2.3	55	37.3	17.7	43	0	6.5	30.8	6.9	45	3.41	3.6	Good		A bit choppy, schedule evident, always cycling could be smoother but ok
EOH1761	Air	Vaillant	VWL 105/6 A 230V S2	10	4.9	2.0	50	37.7	12.3	44	0	5.5	32.1	6.9	46	3.37	3.5	Great	37@-6!	All aligned quite well here, would usually expect higher perfromance, perhaps lower outside temperature is a factor here
EOH2613	Air	Vaillant	VWL 125/6 A 230V S2	12	1.9	6.3		38.1	-38.1	45	1	7.7	30.4	7.5	43	2.98	3.3	OK		This is probably one of the better examples of what happens with extreme oversizing
EOH1109	Air	Vaillant	VWL 75/6 A 230V S2	7	3.3	2.1	45	48.3	-3.3	61	1	6.2	42.1	3.8	35	2.18	3.0	OK		High WC Required, very low % carnot
EOH0543	Air	Vaillant	VWL 125/6 A 230V S2	12	6.7	1.8	45	46.2	-1.2	58	1	5.7	40.5	8.6	45	2.9	3.1	OK		Mix of issues, high temps required, but also some boost high temps at other times, highly variable internal temp
EOH0254	Air	Vaillant	VWL 55/6 A 230V S2	5	2.5	2.0	45	46.1	-1.1	58	1	5.4	40.7	4.6	43	2.76	3.1	OK		Think there is an opportunity for less intermittent and lower WC here
EOH1557	Air	Vaillant	VWL 55/6 A 230V S2	5	4.7	1.1	45	45.6	-0.600000000000001	57	1	5.6	40	4.2	32	2.07	3.1	OK		High WC Required, defrost issues? Air circulation? Very low % carnot
EOH1327	Air	Vaillant	VWL 75/6 A 230V S2	7	2.5	2.8	50	50	0	64	1	7.5	42.5	6.8	42	2.61	3.0	OK		Very high DHW demand coupled with high DHW temps, large setback on space heating..
EOH0033	Air	Vaillant	VWL 125/6 A 230V S2	12	4.8	2.5	45	45	0	56	1	7.3	37.6	9.4	37	2.52	3.3	OK		Something strange here, might be buffer distortion related?
EOH0667	Air	Vaillant	VWL 55/6 A 230V S2	5	4.6	1.1	45	43.6	1.4	54	1	5.8	37.8	5.1	37	2.52	3.3	OK		temperature sensor in garage?? very high temps required, some set backs but not a lot off room to reduce
EOH1365	Air	Vaillant	VWL 55/6 A 230V S2	5	2.9	1.7	45	42.4	2.6	52	1	5.5	36.8	4	41	2.79	3.3	OK		Bit of mixture here of WC that looks ok and some hotter boosts
EOH2612	Air	Vaillant	VWL 75/6 A 230V S2	7	2.9	2.4	45	42.3	2.7	52	1	5.4	36.8	3.9	37	2.43	3.2	OK		Bit of a mix, schedule/setback leads to high temps on recovery, but then WC after is ok
EOH1239	Air	Vaillant	VWL 75/6 A 230V S2	7	5.3	1.3	45	41.7	3.3	51	1	5.1	36.6	5.7	43	2.96	3.3	OK		High temps required but at least some opportunity for more even lower temp,
EOH0335	Air	Vaillant	VWL 55/6 A 230V S2	5	4.4	1.1	45	41.6	3.4	50	1	5.2	36.4	3.9	41	2.84	3.3	OK		Bit of a mix in this one
EOH1544	Air	Vaillant	VWL 125/6 A 230V S2	12	5.5	2.2	50	46.4	3.6	58	1	6	40.4	9.4	43	2.83	3.2	OK		High temps required, but lower curve could be used with smaller setback
EOH1484	Air	Vaillant	VWL 105/6 A 230V S2	10	8.5	1.2	45	41.2	3.8	50	1	5.2	36	8.3	47	2.86	2.9	OK		No heat on hot water, ultrasonic or heat meter on space heat only?
EOH2448	Air	Vaillant	VWL 75/6 A 230V S2	7	5.7	1.2	50	45.9	4.1	57	1	6.1	39.8	4.7	40	2.55	3.1	OK		Fault mid december? Otherwise WC ok?
EOH1254	Air	Vaillant	VWL 75/6 A 230V S2	7	3.1	2.3	45	40.7	4.3	49	1	6.3	34.4	6.2	44	3.17	3.5	OK		Intermittent heating, lower more even WC could be better
EOH0172	Air	Vaillant	VWL 125/6 A 230V S2	12	6	2.0	50	44.9	5.1	56	1	6.7	38.1	7.9	45	2.99	3.2	OK		some 65C boosts, but WC is actice
EOH1363	Air	Vaillant	VWL 125/6 A 230V S2	12	5	2.4	50	43.8	6.2	54	1	6.4	37.4	7.9	46	3.15	3.3	OK		High temps required, a bit off cycling on room temp, but maybe limited by being oversized and perhaps interaction of buffer?
EOH1576	Air	Vaillant	VWL 55/6 A 230V S2	5	3.6	1.4	45	38.3	6.7	45	0	5.5	32.9	3.5	37	2.74	3.6	OK		WC was improved on this one part way through
EOH3003	Air	Vaillant	VWL 125/6 A 230V S2	12	7.7	1.6	45	37.1	7.9	43	0	5.4	31.7	9.3	43	3.3	3.7	OK		Mixed bag, good periods and also plenty of cycling on room temp
EOH1602	Air	Vaillant	VWL 125/6 A 230V S2	12	4.7	2.6	50	41.7	8.3	51	0	4.7	36.9	7	40	2.62	3.1	OK		High temps required, oversized, low % carnot
EOH1392	Air	Vaillant	VWL 55/6 A 230V S2	5	1.6	3.1	50	41.6	8.4	50	0	6.3	35.4	4.7	44	3.08	3.4	OK		Intermittent heating causing higher temp boosts
EOH0324	Air	Vaillant	VWL 75/6 A 230V S2	7	3.6	1.9	50	41.1	8.9	50	0	6.5	34.6	4.4	40	2.65	3.2	OK		System needs to run hot, room temp not that high, very distinct schedule/setback, low % carnot
EOH0474	Air	Vaillant	VWL 55/6 A 230V S2	5	2.1	2.4	50	39.2	10.8	46	0	7.7	31.5	3.4	38	2.92	3.7	OK	46@-3C	Weather comp is set, large setback and schedules, very low % carnot
EOH3014	Air	Vaillant	VWL 55/6 A 230V S2	5	2.9	1.7	50	38.5	11.5	45	0	7.4	31.1	3.9	42	3.16	3.6	OK		Weather comp is set on this, but uses high temp boost to bring house back to temp on schedule
EOH0766	Air	Vaillant	VWL 75/6 A 230V S2	7	2.7	2.6	55	43.3	11.7	53	0	7.4	35.9	5.2	43	3.06	3.4	OK	53@0C	Weather comp is set correctly, high temps required, though large set-back
EOH1042	Air	Vaillant	VWL 75/6 A 230V S2	7	4.5	1.6	55	43.1	11.9	53	0	7	36.1	5.3	45	3.16	3.4	OK	50C@-8	Weather comp set, struggling a bit with max output, some hot water issues
EOH2149	Air	Vaillant	VWL 55/6 A 230V S2	5	2.5	2.0	55	43.1	11.9	53	0	6.3	36.8	3.9	44	3	3.3	OK		Mostly well set weather comp with large set back, a little room temp cycling
EOH1771	Air	Vaillant	VWL 125/6 A 230V S2	12	3.6	3.3	50	38	12	45	0	5.7	32.3	7.1	47	3.3	3.4	OK		Weather comp is set, and often low temp, struggling a bit with oversizing and some DHW control
EOH0065	Air	Vaillant	VWL 75/6 A 230V S2	7	2.5	2.8	50	37.5	12.5	44	0	6.7	30.8	6.8	43	3.31	3.7	OK		Mostly room temp cycling but curve is close
EOH0200	Air	Vaillant	VWL 75/6 A 230V S2	7	2.8	2.5	55	42.1	12.9	51	0	7	35.1	5	40	2.83	3.4	OK	37-52	Weather comp is set, but lots of variation due to schedules / set back, very low % carnot, possibly some room temp cycling
EOH0238	Air	Vaillant	VWL 55/6 A 230V S2	5	2.9	1.7	55	40.3	14.7	48	0	6.6	33.7	3.3	41	3	3.5	OK	~51@-5	Weather comp is set, needs ~50 at designt emp, low % carnot
EOH0222	Air	Vaillant	VWL 75/6 A 230V S2	7	2.5	2.8	55	39.9	15.1	48	0	6.3	33.7	5.1	41	3	3.5	OK		Weather comp is set, maybe a bit too high at times, some room temp cycling, oversized and low % carnot, low space heating demand I think
EOH1663	Air	Vaillant	VWL 75/6 A 230V S2	7	4	1.8	40	48	-8	61	1	6.9	41.2	4.8	44	2.78	3.0	OK/Good	48@-6	Weather comp for space heating is mostly ok, large DHW demand, setback && schedule

Design	WA Flow	WA FMO				Average				Margin	2					Average
55	44.5	37.8	10.5	17.2		2.12				Total	93					2.88	3.30		2.69	2.85	3.3
50	41.3	34.6	8.7	15.4															3.20	3.30	3.5
45	38.3	31.6	6.7	13.4
40	35.2	28.5	4.8	11.5

44.5	55	55
41.3	50	50
38.3	45	45
35.2	40	40

## Table
Description	Number	%	SPF H4	~48% Carnot
Weather comp too high, cycling on room temp	90	54.5%	2.69	3.2
Mixed, harder to classify	34	20.6%	2.85	3.3
Weather comp is generally set quite well, other issues may be present	41	24.8%	3.3	3.5
Total	165	100%	2.88	3.2